## WIO Power Consumption (hidden)
Boomerang Power Consumption Measurement
Supply Voltage | 9V |  | 12V |  | 24V |  | 30V
| (mA) | (mW) | (mA) | (mW) | (mA) | (mW) | (mA) | (mW) | Notes
Radio Module | 42.5 | 382.5 | 34.5 | 414 | 22.5 | 540 | 19.5 | 585 | Avg. (10% duty cycle)
Digital Moudle | 32.6 | 293.4 | 25.8 | 309.6 | 13.6 | 326.4 | 11.5 | 345 | max. (all I/O in active state)
4-20 mA Analog Module | 86.6 | 779.4 | 82.3 | 987.6 | 33.5 | 804 | 34.5 | 1035 | max. (AO = 20 mA)
01-10 V Analog Module | 75.6 | 680.4 | 57.6 | 691.2 | 30 | 720 | 24.3 | 729 | max. (AO = 10V)
Max. Allowable Module
16x Digital | 564.1 | 5076.9 | 447.3 | 5367.6 | 240.1 | 5762.4 | 203.5 | 6105
5x 4-20mA Analog | 475.5 | 4279.5 | 446 | 5352 | 190 | 4560 | 192 | 5760
8x 0-10V Analog | 647.3 | 5825.7 | 495.3 | 5943.6 | 262.5 | 6300 | 213.9 | 6417

## Power Budget Calculator
IO Module
| 9V |  | 12V |  | 24V |  | 30V |  | Digital | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| (mA) | (mW) | (mA) | (mW) | (mA) | (mW) | (mA) | (mW) | 4-20 mA | 0 | 1 | 2 | 3 | 4 | 5
| 42.5 | 382.5 | 34.5 | 414 | 22.5 | 540 | 19.5 | 585 | 0-10 V | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| 32.6 | 293.4 | 25.8 | 309.6 | 13.6 | 326.4 | 11.5 | 345
| 86.6 | 779.4 | 82.3 | 987.6 | 33.5 | 804 | 34.5 | 1035
| 75.6 | 680.4 | 57.6 | 691.2 | 30 | 720 | 24.3 | 729 | Voltage | 9V | 12V | 24V | 30V |  | 9V | 2 |  | 5
[9 empty] | RS485 | 198 | 228 | 312 | 330 |  | 12V | 3
[9 empty] | Digital | 293 | 310 | 326 | 345 |  | 24V | 4
[9 empty] | 4-20 mA | 779 | 988 | 804 | 1035 |  | 30V | 5
[9 empty] | 0-10 V | 680 | 691 | 720 | 729
RS485 Expansion I/O System Power Budget Calculator
| Power Supply Voltage | (mW) | Qty. | Sub-Total (mW) | Note
WIO Module | 30V | Adjust Power and # of I/O Modules |  |  | Select power supply voltage by clicking B16
BM-1000-PM1 | RS485 | 330 | 1 | 330 | Only one RS485 Module per system
BM-D100-144 | Digital | 345 | 0 | 0 | Select the number of Digital Module by clicking D18
BM-A420-122 | 4-20 mA | 1035 | 0 | 0 | Select the number of 4-20 mA Analog Module by clicking D19
BM-A010-122 | 0-10 V | 729 | 0 | 0 | Select the number of 04-10 V Analog Module by clicking D20
| Max. Power Consumption (Watt) |  |  | 0.33 | Maximum allowable power consumption is 6.5W (Class1 Div2)
Total Power Consumption Must Be Less Than 6.5 W
Maximum allowable power consumption is 6.5W (Class1 Div2)