## Interactive Server Map
Input your values |  | Controller tag | internal word address | internal bit address | A master/client addresses our internal memory with these Modbus address |  |  |  | Controller tag | internal word address | internal bit address | A master/client addresses our internal memory with these Modbus address
Read Register Start | 0 | ReadData[0].0 | 0 | 0 | 000001 | -- | -- | 400001 | WriteData[0].0 | 1000 | 16000 | 016001 | 116001 | 301001 | 401001
ReadData[] Index | 0 | ReadData[0].1 | -- | 1 | 000002 | -- | -- | -- | WriteData[0].1 | -- | 16001 | 016002 | 116002 | -- | --
|  | ReadData[0].2 | -- | 2 | 000003 | -- | -- | -- | WriteData[0].2 | -- | 16002 | 016003 | 116003 | -- | --
|  | ReadData[0].3 | -- | 3 | 000004 | -- | -- | -- | WriteData[0].3 | -- | 16003 | 016004 | 116004 | -- | --
Write Register Start | 1000 | ReadData[0].4 | -- | 4 | 000005 | -- | -- | -- | WriteData[0].4 | -- | 16004 | 016005 | 116005 | -- | --
WriteData[] Index | 0 | ReadData[0].5 | -- | 5 | 000006 | -- | -- | -- | WriteData[0].5 | -- | 16005 | 016006 | 116006 | -- | --
|  | ReadData[0].6 | -- | 6 | 000007 | -- | -- | -- | WriteData[0].6 | -- | 16006 | 016007 | 116007 | -- | --
|  | ReadData[0].7 | -- | 7 | 000008 | -- | -- | -- | WriteData[0].7 | -- | 16007 | 016008 | 116008 | -- | --
|  | ReadData[0].8 | -- | 8 | 000009 | -- | -- | -- | WriteData[0].8 | -- | 16008 | 016009 | 116009 | -- | --
Six-place Modbus |  | ReadData[0].9 | -- | 9 | 000010 | -- | -- | -- | WriteData[0].9 | -- | 16009 | 016010 | 116010 | -- | --
registers are shown. |  | ReadData[0].10 | -- | 10 | 000011 | -- | -- | -- | WriteData[0].10 | -- | 16010 | 016011 | 116011 | -- | --
Your registers may |  | ReadData[0].11 | -- | 11 | 000012 | -- | -- | -- | WriteData[0].11 | -- | 16011 | 016012 | 116012 | -- | --
be five-place, like |  | ReadData[0].12 | -- | 12 | 000013 | -- | -- | -- | WriteData[0].12 | -- | 16012 | 016013 | 116013 | -- | --
41001 (401001). |  | ReadData[0].13 | -- | 13 | 000014 | -- | -- | -- | WriteData[0].13 | -- | 16013 | 016014 | 116014 | -- | --
|  | ReadData[0].14 | -- | 14 | 000015 | -- | -- | -- | WriteData[0].14 | -- | 16014 | 016015 | 116015 | -- | --
|  | ReadData[0].15 | -- | 15 | 000016 | -- | -- | -- | WriteData[0].15 | -- | 16015 | 016016 | 116016 | -- | --

## Definitions
Modbus Data |  |  |  |  | Modbus Functions
description | address form | range | bits | R/W | code | Function Description | addresses
Coil | 0xxxx | 00001 to 09999 | 1 | Read-Write | 1 | Read multiple Coils | 0xxxx
| 0xxxxx | 000001 to 065536 |  |  | 2 | Read multiple Discrete Inputs | 1xxxx
Discrete Input | 1xxxx | 10001 to 19999 | 1 | Read-Only | 3 | Read multiple Holding Registers | 4xxxx
| 1xxxxx | 100001 to 165536 |  |  | 4 | Read multiple Input Registers | 3xxxx
Input Register | 3xxxx | 30001 to 39999 | 16 | Read-Only | 5 | Write Single Coil | 0xxxx
| 3xxxxx | 300001 to 365536 |  |  | 6 | Write Single Holding Register | 4xxxx
Holding Register | 4xxxx | 40001 to 49999 | 16 | Read-Write | 15 | Write Multiple Coils | 0xxxx
| 4xxxxx | 400001 to 465536 |  |  | 16 | Write Multiple Holding Registers | 4xxxx
Modbus Command: | [Start] [8-bit node number] [8-bit function code] [data] … [data] [16-bit CRC] [End]
To move 32-bit real data, you COP the real into two consecutive WriteData[] tags.
To receive 32-bit real data, you COP two consecutive ReadData[] tags into a real.
(I hope I have the lengths right.)
rev 2, 3/31/2017

## Memory Map
These settings map controller tag ReadData[] and WriteData[] arrays to module's internal addresses |  | CLX tag | internal word address | internal bit address
Read Register Start | 1000 | WriteData[0] | 0 | 0
Read Register Count | 600 | WriteData[1] | 1 | 16
Write Register Start | 0 | WriteData[2] | 2 | 32
Write Register Count | 600 | WriteData[3] | 3 | 48
|  | WriteData[4] | 4 | 64
|  | WriteData[5].0 | 5 | 80
|  | WriteData[5].1 |  | 81
|  | WriteData[5].2 |  | 82
|  | WriteData[5].3 |  | 83
|  | … | … | …
|  | WriteData[599] | 599 | 9584
|  |  | … | …
|  | ReadData[0] | 1000 | 16000
|  | ReadData[1] | 1001 | 16016
|  | ReadData[2] | 1002 | 16032
|  | ReadData[3] | 1003 | 16048
|  | ReadData[4] | 1004 | 16064
|  | ReadData[5].0 | 1005 | 16080
|  | ReadData[5].1 |  | 16081
|  | ReadData[5].2 |  | 16082
|  | ReadData[5].3 |  | 16083
|  | … | … | …
|  | ReadData[599] | 1599 | 25584
|  |  | … | …

## Master-Client
These settings map controller tag ReadData[] and WriteData[] arrays to module's internal addresses |  | CLX tag | internal word address | internal bit address | Client commands can read-from or write-to these slave Modbus addresses
Read Register Start | 1000 | WriteData[0] | 0 | 0 | 0xxxx | -- | -- | 4xxxx
Read Register Count | 600 | WriteData[1] | 1 | 16
Write Register Start | 0 | WriteData[2] | 2 | 32
Write Register Count | 600 | WriteData[3] | 3 | 48
|  | WriteData[4] | 4 | 64
|  | WriteData[5].0 | 5 | 80
|  | WriteData[5].1 |  | 81
|  | WriteData[5].2 |  | 82
|  | WriteData[5].3 |  | 83
|  | … | … | …
|  | WriteData[599] | 599 | 9584
As a master, we cannot write to 1xxxx Discrete Inputs or 3xxxx Input Registers to a slave. |  |  | … | …
|  | ReadData[0] | 1000 | 16000 | 0xxxx | 1xxxx | 3xxxx | 4xxxx
|  | ReadData[1] | 1001 | 16016
|  | ReadData[2] | 1002 | 16032
|  | ReadData[3] | 1003 | 16048
|  | ReadData[4] | 1004 | 16064
|  | ReadData[5].0 | 1005 | 16080
|  | ReadData[5].1 |  | 16081
|  | ReadData[5].2 |  | 16082
|  | ReadData[5].3 |  | 16083
|  | … | … | …
|  | ReadData[599] | 1599 | 25584
|  |  | … | …

## Slave-Server
These settings map controller tag ReadData[] and WriteData[] arrays to module's internal addresses |  | CLX tag | internal word address | internal bit address | A master/client addresses our internal memory with these Modbus address
Read Register Start | 1000 | WriteData[0] | 0 | 0 | 00001 | 10001 | 30001 | 40001
Read Register Count | 600 | WriteData[1] | 1 | 16 | 00017 | 10017 | 30002 | 40002
Write Register Start | 0 | WriteData[2] | 2 | 32
Write Register Count | 600 | WriteData[3] | 3 | 48
|  | WriteData[4] | 4 | 64
|  | WriteData[5].0 | 5 | 80
|  | WriteData[5].1 |  | 81
|  | WriteData[5].2 |  | 82
|  | WriteData[5].3 |  | 83
|  | … | … | …
|  | WriteData[599] | 599 | 9584
As a slave, a client cannot modify our 1xxxx Discrete Inputs or 3xxxx Input Registers. |  |  | … | …
|  | ReadData[0] | 1000 | 16000 | 016001 | -- | -- | 41001
|  | ReadData[1] | 1001 | 16016
|  | ReadData[2] | 1002 | 16032
|  | ReadData[3] | 1003 | 16048
|  | ReadData[4] | 1004 | 16064
|  | ReadData[5].0 | 1005 | 16080
|  | ReadData[5].1 |  | 16081
|  | ReadData[5].2 |  | 16082
|  | ReadData[5].3 |  | 16083
|  | … | … | …
|  | ReadData[599] | 1599 | 25584
|  |  | … | …

## Server Offsets
These settings map controller tag ReadData[] and WriteData[] arrays to module's internal addresses |  | CLX tag | internal word address | internal bit address | Modbus address
Read Register Start | 1000 | WriteData[0] | 0 | 0 | 30001
Read Register Count | 600 | WriteData[1] | 1 | 16 | 30002
Write Register Start | 0 | WriteData[2] | 2 | 32 | 30003
Write Register Count | 600 | WriteData[3] | 3 | 48 | 30004
|  | WriteData[4] | 4 | 64
|  | WriteData[5].0 | 5 | 80 | 10001
|  | WriteData[5].1 |  | 81 | 10002
|  | WriteData[5].2 |  | 82 | 10003
|  | WriteData[5].3 |  | 83 | 10004
|  | … | … | …
|  | WriteData[599] | 599 | 9584
These settings map module's internal addresses to modbus addresses for access by a client |  |  | … | …
Output Offset (0xxxx) | 1005 | ReadData[0] | 1000 | 16000 | 40001
Bit Input Offset (1xxxx) | 5 | ReadData[1] | 1001 | 16016 | 40002
Holding Register Offset (4xxxx) | 1000 | ReadData[2] | 1002 | 16032 | 40003
Word Input Offset (3xxxx) | 0 | ReadData[3] | 1003 | 16048 | 40004
|  | ReadData[4] | 1004 | 16064
|  | ReadData[5].0 | 1005 | 16080 | 00001
|  | ReadData[5].1 |  | 16081 | 00002
|  | ReadData[5].2 |  | 16082 | 00003
|  | ReadData[5].3 |  | 16083 | 00004
|  | … | … | …
|  | ReadData[599] | 1599 | 25584
|  |  | … | …

## Pass-Through
These settings map controller tag ReadData[] and WriteData[] arrays to module's internal addresses |  | CLX tag | internal word address | internal bit address | possible Modbus address
Read Register Start | 1000 | WriteData[0] | 0 | 0 | 00001 | 10001 | 30001 | 40001
Read Register Count | 600 | WriteData[1] | 1 | 16 | 00017 | 10017 | 30002 | 40002
Write Register Start | 0 | WriteData[2] | 2 | 32
Write Register Count | 600 | WriteData[3] | 3 | 48
|  | WriteData[4] | 4 | 64
|  | WriteData[5].0 | 5 | 80
|  | WriteData[5].1 |  | 81
|  | WriteData[5].2 |  | 82
For Pass-Through: |  | WriteData[5].3 |  | 83
Write Data Start must be 0. |  | … | … | …
Read Data[] is not used. |  | WriteData[599] | 599 | 9584
Data sent bypasses module memory and appears in processor in WriteData[]. |  |  | … | …
(Server offsets can also be set.)